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Location: St James C of E Primary School Greenacre Street Clitheroe BB7 1ED
Proposal: Approval of details reserved by conditions 14 (foul and SW drainage), 16 (SW sustainable drainage strategy), 17 (construction SW management plan), 18 (operation and maintenance manual) and 20 (compensatory flood storage) from planning permission 3/2021/0731.

I write in response to your application to discharge the conditions pursuant to planning approval 

	Condition 14 (Foul and SW Drainage) is a compliance condition which does not require the submission of information.  However, based on the information submitted, United Utilities have raised an objection as no surface water is permitted to discharge into the public sewer network. If this scheme is implemented as proposed then this may result in a breach of this condition. Please note this condition will need to be adhered to in order to satisfy the planning permission.









P.T.O.

	.

Condition 16 (SW Sustainable Drainage Strategy) can be partially discharged as sufficient details have been submitted (Drainage Strategy Part 1 - 5 submitted 21st May, 2024 and Drainage Strategy dated September 2024 by JBA Consulting).  The approved drainage strategy shall be implemented in strict accordance with the approved details.

Condition 17 (Construction SW Management Plan) can be partially discharged as sufficient details have been submitted (Drainage Strategy Part 1 - 5 submitted 21st May, 2024 and Drainage Strategy dated September 2024 by JBA Consulting).  The approved plan shall be implemented and hereafter managed in strict accordance with the approved details for the duration of the construction phase(s).

Condition 18 (Operation and Maintenance Manual) can be partially discharged as sufficient details have been submitted (Drainage Strategy Part 1 - 5 submitted 21st May, 2024 and Drainage Strategy dated September 2024 by JBA Consulting).  The approved drainage system shall be hereafter retained, managed and maintained in strict accordance with the approved details.

Condition 20 (Compensatory Flood Storage) can be partially discharged subject to implementation in strict accordance with the approved details shown in the updated Flood Risk Assessment submitted 9th August 2024 and the mitigation measures identified in drawings:

· Flood Risk Assessment (FRA) prepared by JBA Consulting ref. KPZ_JBAU_00-00-RP-Z-0007 St James Clitheroe FRA S3-P05 dated 5th September 2024
· KPZ_JBA_00-00-DR-HM-0001SO-PO1.01-Compensatory_Storage_Plan.dwg KPZ_JBA_00-00-DR-HM-0002-SO-P01.0_Compensatory_Storage_Section_Views.dwg

The approved scheme shall be hereafter retained, managed and maintained in strict accordance with the approved details.

Any changes to the approved FRA and/or the mitigation drawings identified in the approved drawings will require the submission of a revised scheme.


	


Nicola Hopkins
NICOLA HOPKINS
DIRECTOR OF ECONOMIC DEVELOPMENT AND PLANNING
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